## Chiller Eligibility
[12 empty] | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
Chiller Eligibility Screening Tool 2025
Updated 7/14/2025
Electric chiller incentives are only available for HVAC space cooling applications. Chillers used for industrial process cooling, ice rinks, data centers and refrigerated warehouses may qualify for a custom incentive (see focusonenergy.com/business or call 1.800.762.7077).
Please complete all sections highlighted in this color to determine if your chiller is eligible for Focus on Energy incentives.
Chiller Type and Performance Data
Chiller Type:
Property Type:
| Chiller AHRI Capacity: |  | Tons | enter capacity at AHRI Conditions, not nominal capacity
AHRI Conditions:
Maximum Chiller Efficiency to Qualify for Focus on Energy Incentives
|  | Path A | Path B
| Full Load Efficiency: |  |  | kW/Ton
| Part Load Efficiency (IPLV): |  |  | kW/Ton
Proposed Chiller Efficiency
Chiller performance data must be at the AHRI conditions listed above
| Known Efficiency Rating: | [10 empty] | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
This is equivalent to:
| Full Load Efficiency: |  |  | 0 |  | #N/A |  | #N/A
| Part Load Efficiency (IPLV): |  |  | 0 |  | #N/A |  | #N/A
If IPLV not known, enter part load ratings below to calculate (otherwise skip)
www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf
| Known % Load values are: |  |  | Clear cells C37 to D40 after changing this value
| % Load |  |  |  | kW/ton | EER | IPLV Formula Coefficient
| 100% | [5 empty] | 0.01
| 75% | [5 empty] | 0.42
| 50% | [5 empty] | 0.45
| 25% | [5 empty] | 0.12
|  |  | (link cell B30 to here, kW/ton or EER as appropriate)----> | Calculated IPLV:
Chiller Eligibility and Incentive
Per HVAC/Plumbing Incentive Requirements for Chillers, all kW/ton values should be rounded to three decimal places. This is reflected below.
Chiller Type:
|  | Base Incentive Rate: |  | /ton
|  | Additional Incentive Rate: |  | /ton per 1.0 EER above threshold and per 1.0 IEER above threshold
Max kW/Ton to Qualify
|  | Actual kW/Ton (Rounded to three Decimals) | Path A |  | Path B
| Full Load Efficiency: | #N/A |  | Must select a chiller type first! |  | Must select a chiller type first!
| Part Load Efficiency (IPLV): | #N/A |  | Must select a chiller type first! |  | Must select a chiller type first!
|  |  | Blank |  | Blank
|  | Eligible? | Error - No Chiller Type Selected |  | Error - No Chiller Type Selected
|  | Incentive Rate ($/ton): |  |  | 0
|  | Chiller Capacity (tons): | 0 |  | 0
|  | Total Incentive: | 0 |  | 0
Measure Code
HVAC / PLUMBING INCENTIVE CATALOG - SUPPLEMENTAL DATA SHEET INPUTS | [8 empty] | Path A
Copy the information below onto the supplemental data sheet when submitting your incentive application, or submit the Cooling Eligibility Screening Tool itself. | [8 empty] | Path B
B1 |  | CHILLERS (BUILDING COOLING LOAD) -
INCENTIVE CODE: H2249, H2250, H2251, H2252 , M-H2249, M-H2250, M-H2251, M-H2252
EQUIP # |  | ANNUAL HOURS OF CHILLER OPERATION (hours chiller enabled to provide some cooling to building) |  |  | BUILDING / SPACE DESIGN COOLING LOAD (tons) |  |  | BASE OR TRIM CHILLER?
1
C1 | CHILLERS (BUILDING COOLING LOAD) - | [8 empty] | PAGE 20-21
INCENTIVE CODE: H4712-H4735
EQUIP TYPE |  |  | BUILDING/SPACE DESIGN COOLING LOAD (TONS) |  | BASE OR TRIM CHILLER? |  | CHILLER LOCKOUT TEMPERATURE (°F) |  | CODE COMPLIANCE PATH: A OR B
(Example) Air-Cooled |  |  | 90 |  | Base |  | 53 °F |  | Path A
C2 | CHILLERS (EQUIPMENT PERFORMANCE) - | [8 empty] | PAGE 20-21
INCENTIVE CODE: H4712-H4735
EQUIP # | (A) AHRI RATED CAPACITY (TONS, WHOLE NUMBER) | (B) MAX FULL LOAD (kW/ton) (FROM MEASURE DESCRIPTION PG 21-23) | (C) AHRI RATED FULL LOAD EFFICIENCY (KW/TON, 3 DECIMALS) | (D) MAX PART LOAD (IPLV) (kW/ton) (FROM MEASURE DESCRIPTION PG 20-21) | (E) AHRI RATED PART LOAD EFFICIENCY (IPLV) (KW/TON, 3 DECIMALS) | (F) DELTA EFFICIENCY: ((B - C) + (D - E)) | (G) ADDITIONAL INCENTIVE ($/TON) | (H) BASE INCENTIVE ($/TON) | (I) INCENTIVE RATE ($/TON) (G + H) | REQUESTED INCENTIVE* (A x I)
(Example) Chiller 1 | 95 | 1.16 | 1.12 | 0.88 | 0.84 | 0.08 | $10.00 | 8 | 18 | 1710
Path A
Path B
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
[17 empty] | IECC 2015 Code Requirement [from Table C403.2.3(7)] |  | Focus on Energy Min. Efficiency to Qualify |  | Focus on Energy-Existing Building Incentive per Ton |  | Focus on Energy-New Construction Incentive per Ton
[13 empty] | Chiller Type | Min Tons | Max Tons | =1 when matches proposed chiller | Full Load kW/ton | IPLV | Full Load kW/ton | IPLV | Additional per 1.0 kW/ton | Base Incentive | Additional per 1.0 kW/ton | Base Incentive | Measure Code
Path A
[13 empty] | Air-cooled chiller < 150 tons | 0 | 149.99 | 0 | 1.1881 | 0.87591 | 1.16 | 0.88 | 125 | 8 | 90 | 4 | H4712
[13 empty] | Air-cooled chiller ≥ 150 tons | 150 | 1000000 | 0 | 1.1881 | 0.85714 | 1.16 | 0.86 | 125 | 8 | 90 | 4 | H4713
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) < 75 tons | 0 | 74.99 | 0 | 0.75 | 0.6 | 0.72 | 0.6 | 125 | 8 | 90 | 4 | H4716
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons | 75 | 149.99 | 0 | 0.72 | 0.56 | 0.69 | 0.56 | 125 | 8 | 90 | 4 | H4717
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.66 | 0.54 | 0.63 | 0.54 | 125 | 8 | 90 | 4 | H4718
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 300 tons and < 600 tons | 300 | 599.99 | 0 | 0.61 | 0.52 | 0.58 | 0.52 | 125 | 8 | 90 | 4 | H4719
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 600 tons | 600 | 1000000 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4720
[13 empty] | Water cooled, centrifugal < 150 tons | 0 | 149.99 | 0 | 0.61 | 0.55 | 0.58 | 0.55 | 125 | 8 | 90 | 4 | H4726
[13 empty] | Water cooled, centrifugal ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.61 | 0.55 | 0.58 | 0.55 | 125 | 8 | 90 | 4 | H4727
[13 empty] | Water cooled, centrifugal ≥ 300 tons and < 400 tons | 300 | 399.99 | 0 | 0.56 | 0.52 | 0.53 | 0.52 | 125 | 8 | 90 | 4 | H4728
[13 empty] | Water cooled, centrifugal ≥ 400 tons and < 600 tons | 400 | 599.99 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4729
[13 empty] | Water cooled, centrifugal ≥ 600 tons | 600 | 1000000 | 0 | 0.56 | 0.5 | 0.53 | 0.5 | 125 | 8 | 90 | 4 | H4730
Path B
[13 empty] | Air-cooled chiller < 150 tons | 0 | 149.99 | 0 | 1.2371 | 0.75949 | 1.24 | 0.73 | 125 | 8 | 90 | 4 | H4714
[13 empty] | Air-cooled chiller ≥ 150 tons | 150 | 1000000 | 0 | 1.2371 | 0.74534 | 1.24 | 0.72 | 125 | 8 | 90 | 4 | H4715
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) < 75 tons | 0 | 74.99 | 0 | 0.78 | 0.5 | 0.78 | 0.47 | 125 | 8 | 90 | 4 | H4721
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons | 75 | 149.99 | 0 | 0.75 | 0.49 | 0.75 | 0.46 | 125 | 8 | 90 | 4 | H4722
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.68 | 0.44 | 0.68 | 0.41 | 125 | 8 | 90 | 4 | H4723
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 300 tons and < 600 tons | 300 | 599.99 | 0 | 0.625 | 0.41 | 0.625 | 0.38 | 125 | 8 | 90 | 4 | H4724
[13 empty] | Water cooled, positive displacement (rotary screw or scroll) ≥ 600 tons | 600 | 1000000 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4725
[13 empty] | Water cooled, centrifugal < 150 tons | 0 | 149.99 | 0 | 0.695 | 0.44 | 0.695 | 0.41 | 125 | 8 | 90 | 4 | H4731
[13 empty] | Water cooled, centrifugal ≥ 150 tons and < 300 tons | 150 | 299.99 | 0 | 0.635 | 0.4 | 0.635 | 0.37 | 125 | 8 | 90 | 4 | H4732
[13 empty] | Water cooled, centrifugal ≥ 300 tons and < 400 tons | 300 | 399.99 | 0 | 0.595 | 0.39 | 0.595 | 0.36 | 125 | 8 | 90 | 4 | H4733
[13 empty] | Water cooled, centrifugal ≥ 400 tons and < 600 tons | 400 | 599.99 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4734
[13 empty] | Water cooled, centrifugal ≥ 600 tons | 600 | 1000000 | 0 | 0.585 | 0.38 | 0.585 | 0.35 | 125 | 8 | 90 | 4 | H4735
[13 empty] | kW/ton = 12 / EER | Known Efficiency Rating | Alt rating 1 Units | Alt rating 2 Units | Alt Rating 1 Value Full | Alt Rating 1 Value Part | Alt Rating 2 Value Full | Alt Rating 2 Value Part | Min Efficiency | Max Efficiency
kW/ton = 12 (COP x 3.412)
COP = EER / 3.412
[13 empty] | COP = 12 / (kW/ton) / 3.412 | kW/Ton | EER | COP | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.3 | 1.5
[13 empty] | EER = 12 / kW/ton | EER | kW/Ton | COP | #DIV/0! | #DIV/0! | 0 | 0 | 40 | 8
[13 empty] | EER = COP x 3.412 | COP | kW/Ton | EER | #DIV/0! | #DIV/0! | 0 | 0
Lookup Tables
[12 empty] | Water Cooled Chillers | Air Cooled Chillers | Facility Types |  | Small Biz Eligible Chiller Types |  |  |  |  | Property Type
[12 empty] | 44 deg. F chilled water supply | 44 deg. F chilled water supply | Business |  | Air-cooled chiller < 150 tons |  |  |  |  | Existing Building
[12 empty] | 85 deg. F condenser water entering temp (temp coming back from cooling tower) | 95 deg. F entering air (dry bulb) on the condensing side | Multifamily | M- | Water cooled, positive displacement (rotary screw or scroll) < 75 tons |  |  |  |  | New Construction
[12 empty] | 2.4 gpm/ton flow rate on the chilled water side | 2.4 gpm/ton flow rate on the chilled water side |  |  | Water cooled, positive displacement (rotary screw or scroll) ≥ 75 tons and < 150 tons
[12 empty] | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance | 0.0001 hr ft^2 deg. F/Btu evaporator fouling factor allowance |  |  | Water cooled, centrifugal < 150 tons
3.0 gpm/ton flow rate on the condenser water side
0.00025 hr ft^2 deg. F/Btu condenser fouling factor allowance
[12 empty] | % Load IPLV Calc Lookups | Column 1 | Column 2
[12 empty] | Tons and Total kW | Tons | Total kW
[12 empty] | kW/Ton | kW/ton
[12 empty] | EER | EER
[12 empty] | Short | Eligibility Details
[12 empty] | Blank | Error - No Chiller Type Selected
[12 empty] | Qualifies | YES, Chiller meets full load and part load efficiency requirements
[12 empty] | DNQ | NO, Chiller does not meet full load or part load efficiency requirements
Successful incentive message
Congratulations! Your chiller qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/businesshvac to complete your incentive application upon project completion. Chiller incentives require use of the Supplemental Data Sheet along with the application, which should be completed using the inputs shown below.
Note on H36: Zach Obert: From page 9 of: http://www.ahrinet.org/App_Content/ahri/files/standards%20pdfs/AHRI%20standards%20pdfs/AHRI%20Standard%20550-590%20(I-P)-2011.pdf

## RTU & Split System
[9 empty] | hide | hide | hide | hide | hide |  | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide | hide
RTU and Split System Cooling Eligibility Screening Tool 2025
Updated 7/23/2025
Incentives are for standard HVAC space cooling and heating (if applicable) applications only, with the exception of AHRI listed equipment <5.42 tons (65,000 Btu/h) which may be used in data center and telecom facilities. Rooftop units and split systems ≥5.42 tons used for industrial process cooling, ice rinks, data centers and refrigerated warehouses may qualify for a custom incentive (see focusonenergy.com/business or call 1.800.762.7077). ≥5.42 ton Air Source Heat Pump Split Systems must be installed as a "Complete System". Partial system install may be eligible for a custom incentive. Beginning 6/1/2024, Split System Air-Source Heat Pumps <5.42 tons eligible through Instant Discount Program only. Please see Focus on Energy website for more details.
Please complete all sections highlighted in this color to determine if your project is eligible for Focus on Energy incentives.
Cooling System Type and Performance Data
| Facility Type: | Business
Property Type:
| AHRI Cooling Capacity (tons): |  | 0 |  | Enter capacity at AHRI Conditions, not nominal capacity
Cooling System Type:
Number of A/C or Heat Pump Units:
| Known Cooling Efficiency Rating: |  |  |  | Cooling performance data must be at the AHRI conditions
This is equivalent to:
| Full Load Cooling Efficiency: |  | 0 |  |  | #N/A |  | #N/A
| Part Load Cooling Efficiency: |  | 0 |  |  | #N/A |  | #N/A
Cooling System Eligibility and Incentive
|  | Min to Qualify | Actual Efficiency
| Full Load Cooling Efficiency (SEER2): |  | #N/A | Must select a Cooling System Type first!
| Full Load Cooling Efficiency (EER): |  | #N/A | Must select a Cooling System Type first!
| Part Load Cooling Efficiency (IEER): |  | #N/A | Must select a Cooling System Type first!
Eligible?
| #VALUE! | 0 | #VALUE!
| #VALUE! | 0
| #VALUE! | 0
| AHRI Capacity (tons): | 0
| Incentive Each: | #VALUE!
| Number of A/C or Heat Pump Units: | 0
| Total Incentive: | #VALUE!
| #VALUE! | #VALUE! | #VALUE!
Note: Supplemental Data Sheet inputs apply only to larger systems (≥5.42 tons).
#VALUE! | [7 empty] | Measure Code
Copy the information below onto the supplemental data sheet when submitting your incentive application. | [6 empty] | #VALUE! | #VALUE!
B1 | AIR CONDITIONING SPLIT, PACKAGED, AND AIR SOURCE HEAT PUMP SYSTEMS (≥ 5.42 TONS) INCENTIVE CODE: H4368, H4369, H4370, H4371, H10025, H10026, H10027 | [6 empty] | PAGE 19-20
EQUIP # | (A) AHRI RATED CAPACITY (TONS, 2 DECIMALS) | (B) AHRI RATED PART LOAD EFFICIENCY (IEER, 2 DECIMALS) | (C) PART LOAD EFF TO QUALIFY (IEER) (FROM MEASURE DESCRIPTION PG 19) | (D) DELTA EFFICIENCY (B - C) | (E) ADDITIONAL INCENTIVE (D x $/TON) | (F) BASE INCENTIVE ($/TON) | (G) INCENTIVE RATE ($/TON) (E + F) | REQUESTED INCENTIVE* (A x G)
(Example) AC 1 | 1 @ 15.00 tons | 16 | 15.4 | 0.6 | 3 | 25 | 28 | 420
| @ 0.00 tons | #N/A |  | #N/A | #VALUE! | #VALUE! | #VALUE! | #VALUE!
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
#VALUE! | [7 empty] | Measure Code
Copy the information below onto the supplemental data sheet when submitting your incentive application. | [6 empty] | Split System | #VALUE!
B2 | AIR SOURCE HEAT PUMP SYSTEMS (≥ 5.42 TONS) - INCENTIVE CODE: H10025, H10026, H10027 | [6 empty] | PAGE 19-20
EQUIP # |  |  | EXISTING HEAT SOURCE (Natural Gas, Electric Resistance, Heat Pump) |  |  | EXISTING NATURAL GAS THERMAL EFFICIENCY (%) (IF APPLICABLE)
(Example) HP1 |  |  | Natural Gas |  |  | 85%
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information.
#VALUE! | [7 empty] | Measure Code | Intermediate Calcs
Copy the information below onto the supplemental data sheet when submitting your incentive application. | [6 empty] | #VALUE! | #VALUE! | Size Range: |  | <5.42
B3 | SPLIT SYSTEM AIR CONDITIONING - CONDENSING UNIT ONLY - INCENTIVE CODE H3909 | [6 empty] | PAGE 20 | SEER2 Threshold: |  | N/A
EQUIP # | (A) AHRI RATED CAPACITY (TONS, 2 DECIMALS) | (B) AHRI RATED FULL LOAD EFFICIENCY (EER, 2 DECIMALS) | (C) FULL LOAD EFF TO QUALIFY (EER) (FROM MEASURE DESCRIPTION PG 20) | (D) DELTA EFFICIENCY (B - C) | (E) ADDITIONAL INCENTIVE (D x $/TON) | (F) BASE INCENTIVE ($/TON) | (G) INCENTIVE RATE ($/TON) (E + F) | REQUESTED INCENTIVE* (A x G) | Potential Measure Code: |  | #VALUE!
(Example) AC 1 | 1 @ 15.00 tons | 12 | 11.5 | 0.5 | 2.5 | 20 | 22.5 | 337.5
| @ 0.00 tons | #N/A |  | #N/A | 0 | #VALUE! | #VALUE! | #VALUE! | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
*Focus on Energy may adjust total incentive based on project caps. Please see measure requirements and Terms and Conditions for more information. | [8 empty] | 1: Lookup Tables; 5: Focus Min. Efficiency to Qualify; 9: Existing Building Incentive; 13: New Construction Incentive
[9 empty] | Measure Code | Facility Type | DX Cooling Type | Size Range | SEER2 | EER | IEER | HSPF2 | Base Incentive | Additional Incentive | Incentive is per… | Supplemental Data Sheet | Base Incentive | Additional Incentive | Incentive is per… | Measure Name from Catalog
[9 empty] | H5423 | Data Center and Telecom | Split System | <5.42 | 16 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 40 | 0 | A/C Unit | 16 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5424 | Data Center and Telecom | Split System | <5.42 | 17 | N/A | N/A | N/A | 70 | 0 | A/C Unit | None | 50 | 0 | A/C Unit | 17 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5425 | Data Center and Telecom | Split System | <5.42 | 18 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 60 | 0 | A/C Unit | 18 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5426 | Data Center and Telecom | Split System | <5.42 | 19 | N/A | N/A | N/A | 130 | 0 | A/C Unit | None | 70 | 0 | A/C Unit | 19 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5427 | Data Center and Telecom | Split System | <5.42 | 20 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 90 | 0 | A/C Unit | 20 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5423 | Data Center and Telecom | Packaged | <5.42 | 16 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 40 | 0 | A/C Unit | 16 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5424 | Data Center and Telecom | Packaged | <5.42 | 17 | N/A | N/A | N/A | 70 | 0 | A/C Unit | None | 50 | 0 | A/C Unit | 17 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5425 | Data Center and Telecom | Packaged | <5.42 | 18 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 60 | 0 | A/C Unit | 18 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5426 | Data Center and Telecom | Packaged | <5.42 | 19 | N/A | N/A | N/A | 130 | 0 | A/C Unit | None | 70 | 0 | A/C Unit | 19 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5427 | Data Center and Telecom | Packaged | <5.42 | 20 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 90 | 0 | A/C Unit | 20 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5423 | Business | Split System | <5.42 | 16 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 40 | 0 | A/C Unit | 16 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5424 | Business | Split System | <5.42 | 17 | N/A | N/A | N/A | 70 | 0 | A/C Unit | None | 50 | 0 | A/C Unit | 17 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5425 | Business | Split System | <5.42 | 18 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 60 | 0 | A/C Unit | 18 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5426 | Business | Split System | <5.42 | 19 | N/A | N/A | N/A | 130 | 0 | A/C Unit | None | 70 | 0 | A/C Unit | 19 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5427 | Business | Split System | <5.42 | 20 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 90 | 0 | A/C Unit | 20 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5423 | Business | Packaged | <5.42 | 16 | N/A | N/A | N/A | 50 | 0 | A/C Unit | None | 40 | 0 | A/C Unit | 16 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5424 | Business | Packaged | <5.42 | 17 | N/A | N/A | N/A | 70 | 0 | A/C Unit | None | 50 | 0 | A/C Unit | 17 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5425 | Business | Packaged | <5.42 | 18 | N/A | N/A | N/A | 100 | 0 | A/C Unit | None | 60 | 0 | A/C Unit | 18 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5426 | Business | Packaged | <5.42 | 19 | N/A | N/A | N/A | 130 | 0 | A/C Unit | None | 70 | 0 | A/C Unit | 19 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5427 | Business | Packaged | <5.42 | 20 | N/A | N/A | N/A | 150 | 0 | A/C Unit | None | 90 | 0 | A/C Unit | 20 SEER2 A/C Split System or Single Package, < 5.42 tons
[9 empty] | H5428 | Business | Heat Pump (Split System Only) | <5.42 | 16 | N/A | N/A | 8.5 | N/A | 0 | A/C Unit | None | N/A | 0 | A/C Unit | 16 SEER2 and 8.5 HSPF2 Split System Air-Source Heat Pump, < 5.42 tons
[9 empty] | H5429 | Business | Heat Pump (Split System Only) | <5.42 | 17 | N/A | N/A | 8.5 | N/A | 0 | A/C Unit | None | N/A | 0 | A/C Unit | 17 SEER2 and 8.5 HSPF2 Split System Air-Source Heat Pump, < 5.42 tons
[9 empty] | H5430 | Business | Heat Pump (Split System Only) | <5.42 | 18 | N/A | N/A | 8.5 | N/A | 0 | A/C Unit | None | N/A | 0 | A/C Unit | 18 SEER2 and 8.5 HSPF2 Split System Air-Source Heat Pump, < 5.42 tons
[9 empty] | H5431 | Business | Heat Pump (Split System Only) | <5.42 | 19 | N/A | N/A | 8.5 | N/A | 0 | A/C Unit | None | N/A | 0 | A/C Unit | 19 SEER2 and 8.5 HSPF2 Split System Air-Source Heat Pump, < 5.42 tons
[9 empty] | H5432 | Business | Heat Pump (Split System Only) | <5.42 | 20 | N/A | N/A | 8.5 | N/A | 0 | A/C Unit | None | N/A | 0 | A/C Unit | 20 SEER2 and 8.5 HSPF2 Split System Air-Source Heat Pump, < 5.42 tons
[9 empty] | H4368 | Business | Split System | 5.42-11.24 | N/A | N/A | 16.1 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 5.42 to < 11.25 tons, Min. Eff. = 16.1 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4368 | Business | Packaged | 5.42-11.24 | N/A | N/A | 16.1 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 5.42 to < 11.25 tons, Min. Eff. = 16.1 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4369 | Business | Split System | 11.25-19.99 | N/A | N/A | 15.4 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 11.25 to < 20.00 tons, Min. Eff. = 15.4 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4369 | Business | Packaged | 11.25-19.99 | N/A | N/A | 15.4 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 11.25 to < 20.00 tons, Min. Eff. = 15.4 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4370 | Business | Split System | 20-63.32 | N/A | N/A | 14.3 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 20.00 to < 63.33 tons, Min. Eff. = 14.3 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4370 | Business | Packaged | 20-63.32 | N/A | N/A | 14.3 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 20.00 to < 63.33 tons, Min. Eff. = 14.3 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4371 | Business | Split System | >=63.33 | N/A | 9.7 | 11.4 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 63.33 tons, Min. Eff. = 9.7 EER and 11.4 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H4371 | Business | Packaged | >=63.33 | N/A | 9.7 | 11.4 | N/A | 30 | 5 | ton | B1 | 25 | 3 | ton | DX Cooling ≥ 63.33 tons, Min. Eff. = 9.7 EER and 11.4 IEER (additional incentive on IEER) | Additional incentive is per ton for each 1.0 IEER over baseline
[9 empty] | H3909 | Business | Condensing Unit Only | >=11.25 | N/A | 11.5 | N/A | N/A | 25 | 5 | ton | B3 | 0 | 0 | ton | Split System A/C Condensing Unit Only, ≥11.25 tons, ≥ 11.5 EER | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10025 | Business | Heat Pump (Split System) | 5.42-11.24 | N/A | N/A | 15.1 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 5.42 to < 11.25 tons | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10025 | Business | Heat Pump (Packaged) | 5.42-11.24 | N/A | N/A | 15.1 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 5.42 to < 11.25 tons | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10026 | Business | Heat Pump (Split System) | 11.25-19.99 | N/A | N/A | 14.5 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 11.25 to < 20.00 tons | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10026 | Business | Heat Pump (Packaged) | 11.25-19.99 | N/A | N/A | 14.5 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 11.25 to < 20.00 tons | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10027 | Business | Heat Pump (Split System) | 20-63.32 | N/A | N/A | 13.5 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 20.00 to < 63.33 tons, | Additional incentive is per ton for each 1.0 EER over baseline
[9 empty] | H10027 | Business | Heat Pump (Packaged) | 20-63.32 | N/A | N/A | 13.5 | N/A | 40 | 5 | ton | B1 & B2 | 25 | 3 | ton | Commercial Air Source Heat Pumps, ≥ 20.00 to < 63.33 tons, | Additional incentive is per ton for each 1.0 EER over baseline
Property Type
Existing Building
New Construction
[9 empty] | Facility Types |  | Additional Incentive On:
[9 empty] | Business |  | Split System | IEER
[9 empty] | Data Center and Telecom |  | Packaged | IEER
[11 empty] | Condensing Unit Only | EER
[9 empty] | Efficiency Units Conversion |  |  | Full Load |  |  |  | Part Load
[9 empty] | kW/ton = 12 / EER |  | Known Efficiency Rating | Alt Rating 1 |  | Alt Rating 2 |  | Alt Rating 1 |  | Alt Rating 2
[9 empty] | kW/ton = 12 (COP x 3.412) |  | kW/Ton | #DIV/0! | EER | #DIV/0! | COP | #DIV/0! | EER | #DIV/0! | COP
[9 empty] | COP = EER / 3.412 |  | EER | #DIV/0! | kW/Ton | 0 | COP | #DIV/0! | kW/Ton | 0 | COP
[9 empty] | COP = 12 / (kW/ton) / 3.412 |  | COP | #DIV/0! | kW/Ton | 0 | EER | #DIV/0! | kW/Ton | 0 | EER
[9 empty] | EER = 12 / kW/ton |  | SEER2 | #DIV/0! | kW/Ton | 0 | COP | #DIV/0! | kW/Ton | 0 | COP
EER = COP x 3.412
System Types
[9 empty] | Program & Size: |  | Data Center, <= tons | Business, <5.42 tons | [5 empty] | Business, 5.42-11.24 tons |  |  |  |  | Business, >11.25 tons
[11 empty] | Split System | Split System | [5 empty] | Split System |  |  |  |  | Split System
[11 empty] | Packaged | Packaged | [5 empty] | Packaged |  |  |  |  | Packaged
[12 empty] | Heat Pump (Split System Only) | [5 empty] | Heat Pump (Split System) |  |  |  |  | Heat Pump (Split System)
[18 empty] | Heat Pump (Packaged) |  |  |  |  | Heat Pump (Packaged)
Condensing Unit Only
Successful incentive message
Congratulations! Your project qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/catalogs to complete you incentive application upon project completion. DX Cooling incentives require use of the Supplemental Data Sheet along with the application, which should be completed using the inputs shown below.
Congratulations! Your project qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/catalogs to complete you incentive application upon project completion.
Congratulations! Your Data Center and Telecom Cooling Equipment project qualifies for an incentive. Please use the HVAC/Plumbing Incentive Catalog available at focusonenergy.com/catalogs to complete you incentive application upon project completion.
Supplemental Data Sheet Needed Text
THIS SUPPLEMENTAL DATA SHEET NOT NEEDED FOR THIS FACILITY TYPE & A/C SIZE
HVAC / PLUMBING INCENTIVE CATALOG - SUPPLEMENTAL DATA SHEET INPUTS
Note on P131: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed option as result of 2024 mid-year update.

## Setup (hidden)
# of decimals for "Tons" input: | 0 | Changes Cells D60 and F60 on Chiller Eligibility tab | Hidden Tab
# of decimals for "Additional Incentive" value: | 2 | Changes Cells H91 and H92 on Chiller Eligibility tab