## Linkageless Boiler Control
Focus on Energy Business Programs Deemed Savings Calculation
Tech Code: | 1.0711.085
Group: | Boilers & Burners
Category: | Controls
Description: | Linkageless Boiler Control
Developed by: | Andrew Kotila
Submitted by: | Andrew Kotila
Quality group release date: | 2008-08-22
Evaluation approval date:
Evaluator:
Program Requirements:
1. Incentive Applies to natural gas forced draft boilers 200hp and greater (6.69 million Btu per hour output and greater)
2. Boilers must be for space heating or operate a minimum of 4000 hrs per year
3. Equipment must be purchased and operable prior to submitting an incentive application.
4. Replaced equipment must be removed.
Focus on Energy application form (link valid as of September 2008):
http://focusonenergy.com/files/Document_Management_System/Business_Programs/boilercombustion_incentiveapplication.pdf
Input:
| 50% | boiler load factor (assumed average)
| 80% | boiler efficiency (minimum Wisconsin code value, deemed per modulating boiler measures, May 2008)
| 33469.8055 | Btu/hr per boiler hp (conversion factor per ASHRAE Fundamentals Handbook: 1 bhp = 9.81 kW)
| 4000 | annual boiler operating hours (these are large, usually steam boilers)
Minimum value required to receive incentive is 4000 hours.
Using 4000 hours yields a conservative savings estimate.
Note: Since we ask for operating hours on the form, ideally this variable would be entered into a WISeerts
algorithm for a better estimate. However, that tracking system can only accommodate one variable.
| 3% | savings fraction due to linkageless control retrofit
|  |  | Source: | http://hpac.com/bse/burner-controls-boilers/
Scroll down to the section titled "Ask for guarantees". Quote: "...many engineers report having saved as
much as 5 to 15 percent or more installing a linkageless-control upgrade on an existing burner package."
|  |  | Source: | http://thermalenergyconservation.biz/linkageless.html
Refer to second sentence: "[Installing linkageless combustion controls] typically results in savings in the 3% to 10% range."
|  |  | Source: | Cellucci, Gary, HPAC, Hydronics, Removing Guesswork September/October 2005 | Average savings of 3.1%.
http://www.bizlink.com/HPAC_articles/September2005/38.pdf
Output:
| 25.1024 | annual therm savings per boiler horsepower
Estimated Natural Gas Savings (therms)
per boiler horsepower (output capacity)
|  | due to linkageless control retrofit: | 25.1024 | <--- This is what we seek to have deemed

## Oxygen Trim Control
Focus on Energy Business Programs Deemed Savings Calculation
Tech Code: | 1.0710.085
Group: | Boilers & Burners
Category: | Controls
Description: | Boiler oxygen trim controls [multiple parameter (O2, CO2, and CO) trim controls also qualify]
Developed by: | Andrew Kotila
Submitted by: | Andrew Kotila
Quality group release date: | 2008-08-22
Evaluation approval date:
Evaluator:
Program Requirements:
1. Incentive Applies to natural gas forced draft boilers 200hp and greater (6.69 million Btu per hour output and greater)
2. Boilers must be for space heating or operate a minimum of 4000 hrs per year
3. Equipment must be purchased and operable prior to submitting an incentive application.
4. Replaced equipment must be removed.
Focus on Energy application form (link valid as of September 2008):
http://focusonenergy.com/files/Document_Management_System/Business_Programs/boilercombustion_incentiveapplication.pdf
Input:
| 50% | boiler load factor (assumed average)
| 80% | boiler efficiency (minimum Wisconsin code value, deemed per modulating boiler measures, May 2008)
| 33469.8055 | Btu/hr per boiler hp (conversion factor per ASHRAE Fundamentals Handbook: 1 bhp = 9.81 kW)
| 4000 | annual boiler operating hours (these are large, usually steam boilers)
Minimum value required to receive incentive is 4000 hours.
Using 4000 hours yields a conservative savings estimate.
Note: Since we ask for operating hours on the form, ideally this variable would be entered into a WISeerts
algorithm for a better estimate. However, that tracking system can only accommodate one variable.
| 1.1% | boiler efficiency increase due to oxygen trim or multiple parameter (O2, CO2, and CO) exhaust gas analyzer control retrofit
Using combustion efficiencies based on excess O2 in flue gas (2% and 5% respectively), the efficiency gain on a boiler (with no heat recovery) would be 1.19 percentage points
Using combustion efficiencies based on excess O2 in flue gas, the efficiency gain on a boiler (with heat recovery) would be 0.95 percentage points
These are estimated from tables in Harrell 2002 and other information in the Guide to Industrial Assessments.
|  |  | Source: | Guide to Industrial Assessments for Pollution Prevention and Energy Efficiency
http://www.p2pays.org/ref/19/18351.pdf
|  |  | Source: | Harrell, Ph.D, PE, Greg, Steam System Survey Guide, Oak Ridge Nation Laboratory, ORNL/TM-2001/263, May 2002
http://www1.eere.energy.gov/industry/bestpractices/pdfs/steam_survey_guide.pdf
Output:
| 11.3492 | annual therm savings per boiler horsepower
Estimated Natural Gas Savings (therms)
per boiler horsepower (output capacity)
|  | due to oxygen trim control retrofit: | 11.3492 | <--- This is what we seek to have deemed

## Oxygen Trim Eff Est
Excess Air | O2 % | CO2% | Net Stack Temperature (Flue gas temp – combustion air temp) | [7 empty] | O2 % | (Flue gas temp – combustion air temp)
|  |  | 220 | 230 | 240 | 246 | 250 | 260 | 270 |  |  | 230 | 250 | 270 | 290 | 310 | 330 | 350 | 370 | 390 | 410 | 430 | 450 | 470 | 490 | 510
0 | 0 | 11.8 | 85.3 | 85.1 | 84.9 | 84.8 | 84.7 | 84.5 | 84.2 |  | 1 | 14.49 | 14.92 | 15.36 | 15.79 | 16.23 | 16.67 | 17.11 | 17.55 | 17.99 | 18.43 | 18.88 | 19.32 | 19.77 | 20.21 | 20.66
2.2 | 0.5 | 11.5 | 85.2 | 85 | 84.8 | 84.7 | 84.6 | 84.4 | 84.1 |  | 2 | 14.72 | 15.17 | 15.63 | 16.09 | 16.55 | 17.01 | 17.47 | 17.93 | 18.39 | 18.86 | 19.32 | 19.79 | 20.26 | 20.73 | 21.2
4.5 | 1 | 11.2 | 85.1 | 84.9 | 84.7 | 84.6 | 84.5 | 84.2 | 84 |  | 3 | 14.98 | 15.46 | 15.94 | 16.42 | 16.9 | 17.38 | 17.87 | 18.36 | 18.84 | 19.33 | 19.82 | 20.31 | 20.8 | 21.3 | 21.79
6.9 | 1.5 | 11 | 85 | 84.8 | 84.6 | 84.5 | 84.4 | 84.1 | 83.9 |  | 4 | 15.26 | 15.77 | 16.28 | 16.79 | 17.29 | 17.81 | 18.32 | 18.83 | 19.35 | 19.86 | 20.38 | 20.9 | 21.41 | 21.93 | 22.46
9.5 | 2 | 10.7 | 84.9 | 84.7 | 84.5 | 84.3 | 84.2 | 84 | 83.8 |  | 5 | 15.59 | 16.12 | 16.66 | 17.2 | 17.74 | 18.28 | 18.82 | 19.36 | 19.91 | 20.46 | 21 | 21.55 | 22.1 | 22.65 | 23.2
12.1 | 2.5 | 10.4 | 84.8 | 84.6 | 84.4 | 84.2 | 84.1 | 83.9 | 83.7 |  | 6 | 15.96 | 16.52 | 17.1 | 17.67 | 18.24 | 18.82 | 19.39 | 19.97 | 20.55 | 21.13 | 21.71 | 22.29 | 22.88 | 23.46 | 24.05
15 | 3 | 10.1 | 84.7 | 84.5 | 84.2 | 84.1 | 84 | 83.8 | 83.5 |  | 7 | 16.38 | 16.98 | 17.59 | 18.2 | 18.82 | 19.43 | 20.04 | 20.66 | 21.28 | 21.9 | 22.52 | 23.14 | 23.77 | 24.39 | 25.02
18 | 3.5 | 9.8 | 84.6 | 84.4 | 84.1 | 84 | 83.9 | 83.6 | 83.4 |  | 8 | 16.86 | 17.51 | 18.16 | 18.82 | 19.48 | 20.14 | 20.8 | 21.46 | 22.12 | 22.79 | 23.46 | 24.12 | 24.79 | 25.47 | 26.14
21.1 | 4 | 9.6 | 84.5 | 84.2 | 84 | 83.8 | 83.7 | 83.5 | 83.2 |  | 9 | 17.42 | 18.13 | 18.83 | 19.54 | 20.25 | 20.96 | 21.68 | 22.39 | 23.11 | 23.83 | 24.55 | 25.27 | 25.99 | 26.72 | 27.44
24.5 | 4.5 | 9.3 | 84.3 | 84.1 | 83.8 | 83.7 | 83.6 | 83.3 | 83.1 |  | 10 | 18.09 | 18.86 | 19.62 | 20.39 | 21.16 | 21.94 | 22.71 | 23.49 | 24.27 | 25.05 | 25.83 | 26.62 | 27.41 | 28.19 | 28.98
28.1 | 5 | 9 | 84.2 | 83.9 | 83.7 | 83.5 | 83.4 | 83.2 | 82.9 |  | 11 | 18.89 | 19.73 | 20.57 | 21.42 | 22.26 | 23.11 | 23.96 | 24.81 | 25.67 | 26.52 | 27.38 | 28.24 | 29.1 | 29.97 | 30.83
31.9 | 5.5 | 8.7 | 84.1 | 83.8 | 83.5 | 83.4 | 83.3 | 83 | 82.7 |  | 12 | 19.87 | 20.8 | 21.73 | 22.66 | 23.6 | 24.54 | 25.48 | 26.43 | 27.37 | 28.32 | 29.27 | 30.22 | 31.18 | 32.13 | 33.09
35.9 | 6 | 8.4 | 83.9 | 83.6 | 83.3 | 83.2 | 83.1 | 82.8 | 82.5 |  | Source: http://www1.eere.energy.gov/industry/bestpractices/pdfs/steam_survey_guide.pdf
40.3 | 6.5 | 8.2 | 83.7 | 83.4 | 83.2 | 83 | 82.9 | 82.6 | 82.3
44.9 | 7 | 7.9 | 83.5 | 83.3 | 83 | 82.8 | 82.7 | 82.4 | 82.1 | [18 empty] | 1.07
49.9 | 7.5 | 7.6 | 83.4 | 83.1 | 82.8 | 82.6 | 82.5 | 82.2 | 81.9 |  | Efficiency Estimates
55.3 | 8 | 7.3 | 83.1 | 82.8 | 82.5 | 82.3 | 82.2 | 81.9 | 81.6 |  | O2 % | (Flue gas temp – combustion air temp) | [15 empty] | 377
61.1 | 8.5 | 7 | 82.9 | 82.6 | 82.3 | 82.1 | 82 | 81.6 | 81.3 |  |  | 230 | 250 | 270 | 290 | 310 | 330 | 350 | 370 | 390 | 410 | 430 | 450 | 470 | 490 | 510
67.3 | 9 | 6.7 | 82.7 | 82.3 | 82 | 81.8 | 81.7 | 81.4 | 81 |  | 1 | 14.49 | 14.92 | 15.36 | 15.79 | 16.23 | 16.67 | 17.11 | 17.55 | 17.99 | 18.43 | 18.88 | 19.32 | 19.77 | 20.21 | 20.66
74.2 | 9.5 | 6.5 | 82.4 | 82.1 | 81.7 | 81.5 | 81.4 | 81 | 80.7 |  | 2 | 14.72 | 15.17 | 15.63 | 16.09 | 16.55 | 17.01 | 17.47 | 17.93 | 18.39 | 18.86 | 19.32 | 19.79 | 20.26 | 20.73 | 21.2 | 1.43
81.6 | 10 | 6.2 | 82.1 | 81.8 | 81.4 | 81.2 | 81.1 | 80.7 | 80.3 |  | 3 | 14.98 | 15.46 | 15.94 | 16.42 | 16.9 | 17.38 | 17.87 | 18.36 | 18.84 | 19.33 | 19.82 | 20.31 | 20.8 | 21.3 | 21.79
89.8 | 10.5 | 5.9 | 81.8 | 81.4 | 81.1 | 80.9 | 80.7 | 80.3 | 79.9 |  | 4 | 15.26 | 15.77 | 16.28 | 16.79 | 17.29 | 17.81 | 18.32 | 18.83 | 19.35 | 19.86 | 20.38 | 20.9 | 21.41 | 21.93 | 22.46
98.7 | 11 | 5.6 | 81.5 | 81.1 | 80.7 | 80.5 | 80.3 | 79.9 | 79.5 |  | 5 | 15.59 | 16.12 | 16.66 | 17.2 | 17.74 | 18.28 | 18.82 | 19.36 | 19.91 | 20.46 | 21 | 21.55 | 22.1 | 22.65 | 23.2
108.7 | 11.5 | 5.3 | 81.1 | 80.7 | 80.3 | 80.1 | 79.7 | 79.4 | 79 |  | 6 | 15.96 | 16.52 | 17.1 | 17.67 | 18.24 | 18.82 | 19.39 | 19.97 | 20.55 | 21.13 | 21.71 | 22.29 | 22.88 | 23.46 | 24.05
119.7 | 12 | 5.1 | 80.6 | 80.2 | 79.8 | 79.4 | 79.4 | 78.9 | 78.5 |  | 7 | 16.38 | 16.98 | 17.59 | 18.2 | 18.82 | 19.43 | 20.04 | 20.66 | 21.28 | 21.9 | 22.52 | 23.14 | 23.77 | 24.39 | 25.02
[11 empty] | 8 | 16.86 | 17.51 | 18.16 | 18.82 | 19.48 | 20.14 | 20.8 | 21.46 | 22.12 | 22.79 | 23.46 | 24.12 | 24.79 | 25.47 | 26.14
[11 empty] | 9 | 17.42 | 18.13 | 18.83 | 19.54 | 20.25 | 20.96 | 21.68 | 22.39 | 23.11 | 23.83 | 24.55 | 25.27 | 25.99 | 26.72 | 27.44
[11 empty] | 10 | 18.09 | 18.86 | 19.62 | 20.39 | 21.16 | 21.94 | 22.71 | 23.49 | 24.27 | 25.05 | 25.83 | 26.62 | 27.41 | 28.19 | 28.98
[11 empty] | 11 | 18.89 | 19.73 | 20.57 | 21.42 | 22.26 | 23.11 | 23.96 | 24.81 | 25.67 | 26.52 | 27.38 | 28.24 | 29.1 | 29.97 | 30.83
[11 empty] | 12 | 19.87 | 20.8 | 21.73 | 22.66 | 23.6 | 24.54 | 25.48 | 26.43 | 27.37 | 28.32 | 29.27 | 30.22 | 31.18 | 32.13 | 33.09
[10 empty] | Efficiency Improvement |  |  | 0.95 |  |  | 1.19
Efficiency Difference |  | w/ Heat Recovery Components |  |  | w/o Heat recovery components
|  | 0.95 |  |  | 1.19
| Average | 1.07
| Use | 1.1
Note on F68: Brian Dunn: An O2 trim control should be able to control excess O2 in flue gas from 1.5 to 3.0 % (2% is optimum) A traditional controller should be able to control excess O2 in the flue gas from 3.0 to 7.0 %. The controls savings will interact with boiler tune-up savings. Assume pre- and post- operation at optimum efficiency and same flue gas temp. Assume flue gas temp is 100 deg above saturated steam temp. If we assume 10 psi as the system steam pressure (HVAC only), saturated steam temp is 240 degrees. Flue gas then is 340 degrees. Assume combustion air is drawn from outside with an average temp of 30.8 deg F (based on TMY2 data from Oct. 1 to April 30) (Note: a higher ambient air temp will reduce savings estimates.) Net flue gas temp is 309 deg F (use 310 deg F to match table).
Note on C68: Brian Dunn: Control savings will also interact with economizers and combustion air preheaters. Assume Net flue gas temp is 50 degrees less due to heat recovery 259 deg F. (use 250 degrees F to match table)

## Linkageless Savings Estimate
Firing Rate | EfficiencyMech | Eff. Linkageless
1 | 83% | 83%
2 | 81% | 83%
3 | 78% | 82.5%
4 | 77% | 82%
5 | 76% | 81.5%
6 | 79% | 82.5%
7 | 80% | 82%
8 | 82.5% | 83%
9 | 77% | 81.5%
10 | 78% | 81.5%
| 79.15% | 82.25% | 3.1% | ave savings
[5 empty] | Source: | Cellucci, Gary, HPAC, Hydronics, Removing Guesswork September/October 2005
http://www.bizlink.com/HPAC_articles/September2005/38.pdf

## Steam Table
Col. 1 | Col. 2 | Col. 3 | Col. 4 | Col. 5 | Col. 6 | Col. 7 | Col. 8
Gauge | Absolute | Steam | Heat of | Latent | Total Heat | Specific | Specific
Pressure | Pressure | Temp. | Sat. Liquid | Heat | of Steam | Volume of | Volume of
| (psia) | (°F) | (Btu/lb) | (Btu/lb) | (Btu/lb) | Sat. Liquid | Sat. Steam
[6 empty] | (cu ft/lb) | (cu ft/lb)
29.743 | 0.08854 | 32 | 0 | 1075.8 | 1075.8 | 0.096022 | 3306
29.515 | 0.2 | 53.14 | 21.21 | 1063.8 | 1085 | 0.016027 | 1526
27.886 | 1 | 101.74 | 69.7 | 1036.3 | 1106 | 0.016136 | 333.6
19.742 | 5 | 162.24 | 130.13 | 1001 | 1131 | 0.016407 | 73.52
9.562 | 10 | 193.21 | 161.17 | 982.1 | 1143.3 | 0.01659 | 38.42
7.536 | 11 | 197.75 | 165.73 | 979.3 | 1145 | 0.01662 | 35.14
5.49 | 12 | 201.96 | 169.96 | 976.6 | 1146.6 | 0.016647 | 32.4
3.454 | 13 | 205.88 | 173.91 | 974.2 | 1148.1 | 0.016674 | 30.06
1.418 | 14 | 209.56 | 177.61 | 971.9 | 1149.5 | 0.016699 | 28.04
0 | 14.696 | 212 | 180.07 | 970.3 | 1150.4 | 0.016715 | 26.8
1.3 | 16 | 216.32 | 184.42 | 967.6 | 1152 | 0.016746 | 24.75
2.3 | 17 | 219.44 | 187.56 | 965.5 | 1153.1 | 0.016768 | 23.39
5.3 | 20 | 227.96 | 196.16 | 960.1 | 1156.3 | 0.01683 | 20.09 | -12.11
10.3 | 25 | 240.07 | 208.42 | 952.1 | 1160.6 | 0.016922 | 16.3
15.3 | 30 | 250.33 | 218.82 | 945.3 | 1164.1 | 0.017004 | 13.75 | 10.26
20.3 | 35 | 259.28 | 227.91 | 939.2 | 1167.1 | 0.017078 | 11.9
25.3 | 40 | 267.25 | 236.03 | 933.7 | 1169.7 | 0.017146 | 10.5
30.3 | 45 | 274.44 | 243.36 | 928.6 | 1172 | 0.017209 | 9.4
40.3 | 55 | 287.07 | 256.3 | 919.6 | 1175.9 | 0.017325 | 7.79
50.3 | 65 | 297.97 | 267.5 | 911.6 | 1179.1 | 0.017429 | 6.66
60.3 | 75 | 307.6 | 277.43 | 904.5 | 1181.9 | 0.017524 | 5.82
70.3 | 85 | 316.25 | 286.39 | 897.8 | 1184.2 | 0.017613 | 5.17
80.3 | 95 | 324.12 | 294.56 | 891.7 | 1186.2 | 0.017696 | 4.65
90.3 | 105 | 331.36 | 302.1 | 886 | 1188.1 | 0.017775 | 4.23
100 | 114.7 | 337.9 | 308.8 | 880 | 1188.8 | 0.01785 | 3.88
110.3 | 125 | 344.33 | 315.68 | 875.4 | 1191.1 | 0.017922 | 3.59
120.3 | 135 | 350.21 | 321.85 | 870.6 | 1192.4 | 0.017991 | 3.33
125.3 | 140 | 353.02 | 324.82 | 868.2 | 1193 | 0.018024 | 3.22
130.3 | 145 | 355.76 | 327.7 | 865.8 | 1193.5 | 0.018057 | 3.11
140.3 | 155 | 360.5 | 333.24 | 861.3 | 1194.6 | 0.018121 | 2.92
150.3 | 165 | 365.99 | 338.53 | 857.1 | 1195.6 | 0.018183 | 2.75
160.3 | 175 | 370.75 | 343.57 | 852.8 | 1196.5 | 0.018244 | 2.6
180.3 | 195 | 379.67 | 353.1 | 844.9 | 1198 | 0.01836 | 2.34
200.3 | 215 | 387.89 | 361.91 | 837.4 | 1199.3 | 0.01847 | 2.13
225.3 | 240 | 397.37 | 372.12 | 828.5 | 1200.6 | 0.018602 | 1.92
250.3 | 265 | 406.11 | 381.6 | 820.1 | 1201.7 | 0.018728 | 1.74
| 300 | 417.33 | 393.84 | 809 | 1202.8 | 0.018896 | 1.54
| 400 | 444.59 | 424 | 780.5 | 1204.5 | 0.01934 | 1.16
| 450 | 456.28 | 437.2 | 767.4 | 1204.6 | 0.019547 | 1.03
| 500 | 467.01 | 449.4 | 755 | 1204.4 | 0.019748 | 0.93
| 600 | 486.21 | 471.6 | 731.6 | 1203.2 | 0.02013 | 0.77
| 900 | 531.98 | 526.6 | 668.8 | 1195.4 | 0.02123 | 0.5
| 1200 | 567.22 | 571.7 | 611.7 | 1183.4 | 0.02232 | 0.36
| 1500 | 596.23 | 611.6 | 556.3 | 1167.9 | 0.02346 | 0.28
| 1700 | 613.15 | 636.3 | 519.6 | 1155.9 | 0.02428 | 0.24
| 2000 | 635.82 | 671.7 | 463.4 | 1135.1 | 0.02565 | 0.19
| 2500 | 668.13 | 730.6 | 360.5 | 1091.1 | 0.0286 | 0.13
| 2700 | 679.55 | 756.2 | 312.1 | 1068.3 | 0.03027 | 0.11
| 3206.2 | 705.4 | 902.7 | 0 | 902.7 | 0.05053 | 0.05